NOTE:  The Section 01650 "Starting of Systems” includes detailed procedural requirements for building system start up and system demonstration.  Provide direct reference to individual product specification sections.   ”Revise paragraphs carefully to reflect specific project requirements, or delete them if they do not apply.

The header and footer for each page of the Project Manual shall match the format, font (Times New Roman), size (11 pt), font style (BOLD & CAPITALIZED) and line boarders, of the header and footer shown herein.. The header of each page shall contain the Section Number, the Section Title, and the page number & number of pages as shown herein. The footer shall contain the project number in the right hand side as shown herein, including the Table of Contents.  Division 0 and 1 contain a revision date in the left side of the footer This date is to remain as it is for Department informational purposes only and should not be altered by the Architect/Engineer.

DO NOT include Paragraphs or parts of Paragraphs in the project manual, which have no applicability to the specific project.  KEEP IN NUMERICAL SEQUENCE, If A PART IS NOT USED OR ELIMINATED THEN RENUMBER THE FOLLOWING SECTIONS.  IF A PART IS NOT APPLICABLE TO A SPECIFIC PROJECT THEN DESIGNATE IT AS (NOT APPLICABLE).  Also, please review the General Conditions carefully and coordinate the requirements of those Articles including the Definitions.

# PART 1 - GENERAL

## RELATED DOCUMENTS

### A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

## SUMMARY

### This Section includes administrative and procedural requirements for handling requests for building system start up and system demonstration and includes the following:

NOTE:  Edit the following listing depending on whether the relevant article is contained within the final edited section or not

#### Starting Systems.

#### Demonstration and instructions.

#### Testing, adjusting, and balancing.

### Related Sections: The following Sections contain requirements that relate to this Section:

NOTE:  Edit the following references if the Sections below are included in this project.

#### Division 1 Section 01400 "Quality Control" specifies quality assurance and inspecting services.

#### Division 1 Section 01700 "Contract Closeout” specifies requirements for contract close out requirements for system operation and maintenance data and extra materials.

NOTE:  Insert the appropriate section reference in paragraph below if system commissioning is provided, otherwise delete paragraph.

#### Division 2, Section “     ” specifies requirements system commissioning.

## STARTING SYSTEMS

### Coordinate schedule for start-up of various equipment and systems.

NOTE:  Insert the required number of day for notification prior to start-up of any systems.

### Provide written notification to the Construction Administrator (30) Calendar Days prior to start-up of each item.

### Verify that each piece of equipment or system has been checked for proper lubrication, drive rotation, belt tension, and control sequence for other conditions that may cause damage.

### Verify that tests, meter readings, and specified electrical characteristics agree with those required by the equipment or system manufacturer.

### Verify in wiring and support components are complete and tested.

NOTE  Include paragraphs below if it is considered an advantage of requiring the contractor to have the manufacturers field services in relationship to scope and complexity of project.  Edit or delete paragraphs that are not applicable to project.

### Execute the start-up under supervision of manufacturer’s representative, in accordance with manufacturer’s instructions.

### When referenced in individual specification sections, require manufacturer to provide an authorized representative to be present at the site to inspect, check, and approve equipment or system installation prior to start-up, and to supervise placing equipment or system in operation.

NOTE  Section 1400 “Quality Control” describes administrative procedures associated with the following paragraph.

### Submit a written report in accordance Section 01400 “Quality Control” that the equipment or system has been properly installed and is functioning properly.

## DEMONSTRATION AND INSTRUCTIONS

NOTE:  Revise subparagraph below if necessary to allow more or less time to than the 2 weeks notification specified.

### Demonstrate operation and maintenance of Products to Owner and Agency Personnel (2) two weeks prior to substantial completion.

NOTE:  Revise any requirements in paragraph below for special classroom instruction as appropriate for project.

### Demonstrate Project equipment and instruct in a classroom environment at location designated by the Construction Administrator and instructed by a qualified manufacturer’s representative who is knowledgeable about the project.

### For equipment or systems requiring seasonal operation perform demonstration for season within (6) six months.

### Utilize operation and maintenance manuals as basis for instruction.  Review contents of manual with Owner and Agency Personnel in detail to explain all aspects of operation and maintenance.

### Demonstrate start-up, operation, control, adjustment, troubleshooting, servicing, and maintenance, and shutdown of each item at agreed upon scheduled time and at equipment or designated location.

### Prepare and insert additional data in operations and maintenance manuals when need for additional data becomes apparent during demonstration.

NOTE:  Consider adding special requirements that exceed those specified.  Possibilities include videocassette recordings for instruction of the owner's personnel.

## TESTING ADJUSTING, AND BALANCING

### The Contractor will employ and pay for the testing services of an independent consultant to verify the testing, adjusting, and balancing.

### Reports will be submitted by the independent testing consultant to the Construction Administrator indicating observations and results of tests and indicating compliance or non-compliance with the requirements of the Contract Documents.

### The Owner may employ and pay for the services of an independent consultant to verify testing, adjusting, and balancing which was performed by the Contractor.

# PART 2 - PRODUCTS (Not Applicable)

# PART 3 - EXECUTION (Not Applicable)

END OF SECTION 01650